## TDH with pump curves
TDH CALCULATIONS FOR SYSTEM CURVE
Assumes f = 0.022 for 2 inch pipe typical operating range
Static Head in Feet = Measured/Estimated
Friction Head in Feet = (fLv2)/(2gD) = (2.1355 x 10-5)LQ2 (Q in gpm, L in feet)
Pressure Head in Feet = 0.10524(Q/No. Mod.)2 (Q in gpm) from Orifice Equations
BOX 1. | [6 empty] | BOX 2.
Q (gpm) | No. Mod. | L (feet) | hstat (feet) | hf (feet) | hp (feet) | TDH | 2" FORCE MAIN EQUIVALENT LENGTH ESTIMATE
0 | 3 | 208 | 10 | 0 | 0 | 10 | Element | 2" Flg. Eq. Length | Number | Eq. Length
10 | 3 | 208 | 10 | 0.44418 | 1.1693 | 11.6135 | Length | 50 | 1 | 50
20 | 3 | 208 | 10 | 1.7767 | 4.6773 | 16.4541 | Reg. 90 deg | 9 | 3 | 27
30 | 3 | 208 | 10 | 3.9977 | 10.524 | 24.5217 | Reg. 45 deg | 4 | 5 | 20
40 | 3 | 208 | 10 | 7.1069 | 18.7093 | 35.8163 | T (Diversion) | 11 | 5 | 55
50 | 3 | 208 | 10 | 11.1046 | 29.2333 | 50.3379 | Coupling (Disconnect) | 2 | 1 | 2
60 | 3 | 208 | 10 | 15.9906 | 42.096 | 68.0866 | 4 Way Cross | 3.5 | 0 | 0
70 | 3 | 208 | 10 | 21.765 | 57.2973 | 89.0623 | Ball Valve (fully open) | 54 | 1 | 54
80 | 3 | 208 | 10 | 28.4278 | 74.8373 | 113.2651
90 | 3 | 208 | 10 | 35.9789 | 94.716 | 140.6949 | TOTAL EQ. LENGTH |  |  | 208
BOX 3 - Programmable Timer Settings
Anticipated pump flow rate |  |  |  | 50 | gpm | From system versus pump curve for selected pump. (See Notes 6 & 7)
Treatment design flow |  |  |  | 600 | gpd | From design flow for facility (i.e. 400 for 3 bedrooms, 500 for 4 bedrooms)
Drainback volume per dose |  |  |  | 8 | gal. | 16 gallons per 100 feet of 2 inch force main if applicable
Dosing Interval (pump rest time) |  |  |  | 2 | hrs. | Typically 2 hrs. for single pass
Number of doses |  |  |  | 12 | d-1
Drainback volume per day |  |  |  | 96 | gpd
Pump design flow |  |  |  | 696 | gpd | (Treatment plus Drainback)
Approx.volume per dose |  |  |  | 58 | gal.
Dose volume per module |  |  |  | 16.6667 | gal. | Should be between 7 and 12.5 Gals. Note this includes gallons in force main
Pump run time per dose |  |  |  | 1.16 | min.
Pump run time per dose |  |  |  | 69.6 | sec.
Tank volume (gal. per inch) ESTIMATE |  |  |  | 20 | gal. in.-1 | From pump tank dimensions or manufacturers' data
Draw down per dose |  |  |  | 2.9 | in. | Prior to drainback
Pump curves shown are suggestive and calculations should be checked against most recent curve data.
Contact MwM is you would like a pump added to the list.
Pa
INSTRUCTIONS: If these instructions do not show up on initial view, change view to normal by selecting View ---> Normal (Cells) to be filled in are in BLUE! BOX 1: 1. Enter the number of modules. (B8) 2. Enter the static head. (D8) BOX 2: 3. Enter the pipe length in BOX 2. (L9) 4. Enter the number of fittings in BOX 2. (M10 THRU M15) 5. TDH is automatically plotted on the pump curves below 6. Choose desired pump. Proper pump selection is where the two curves intersect near the middle of each . 7. Estimate the pump flow rate (GPM) where the curves intersect. BOX 3: 8. Enter anticipated pump flow rate. (E22) 9. Enter design flow (E23) and dosing interval. (E25) 10. Enter pump tank volume (gal./inch). (E33) 11. Verify dose volume per module (E30) is between 7 & 12.5 gal . If not, this cell will be RED. In most cases, decrease the dosing interval (E25) until this is met indicated by a GREEN cell. i.e. Try 1.75 first then 1.5. ******* Printing Instructions********* 12. Print page and insert into drawing package. 13. Print pump curve by clicking once on the desired pump curve and then print.

## Pump Sheet (hidden)
Sta-Rite Pumps
Zoeller | N-98 | 137 |  |  | 140 | 153/55/57/59 |  | 161 |  | 163 | 188 | 189 |  | EC2 |  | EC3
|  | Total dynamic Head |  | Flow | TDH | TDH |  | TDH | Flow | TDH | TDH | TDH |  | TDH | Flow | TDH
| 23 | 26 |  | 0 | 46 | 18.5 |  | 57 | 0 | 67 | 90 | 109 |  | 32 | 0 | 21
| 22.5 | 24 |  | 10 | 43 | 17.5 |  | 54 | 10 | 62 | 87 | 105 |  | 31 | 10 | 20.5
| 21 | 23 |  | 20 | 40 | 14 |  | 51 | 20 | 58 | 83 | 98 |  | 28 | 20 | 18
| 18 | 21 |  | 30 | 37.5 | 12 |  | 48 | 30 | 52 | 78 | 92 |  | 24 | 30 | 17
| 16.5 | 19 |  | 40 | 34 | 7 |  | 42 | 40 | 46 | 74 | 88 |  | 18 | 40 | 12.5
| 13 | 17.5 |  | 50 | 29 |  |  | 38 | 50 | 37 | 70 | 80 |  | 13 | 50 | 8
| 11 | 16 |  | 60 | 24 |  |  | 32 | 60 | 19 | 65 | 75 |  | 6 | 60
| 7 | 13 |  | 70 | 18.5 |  |  | 27 | 70 |  | 60 | 60 |  |  | 70
|  | 9 |  | 80 | 12.5 |  |  | 19 | 80 |  | 57 | 57 |  |  | 80
|  | 6.5 |  | 90 | 6 |  |  | 12 | 90 |  | 50 | 50 |  |  | 90
[8 empty] | 7 | 100 |  | 42 | 43 |  |  | 100
[9 empty] | Hydromatic |  |  |  |  | Myers Pumps | ME-40 | Flow (GPM) | ME-50
|  | Goulds | Flow | WE05H | WE03L | WE03M | EP05 |  | Sheff33 | GPM | TDH | SPD50H | SP50 |  | TDH
|  |  | 0 | 46 | 25 | 28 | 32 |  | 36 | 0 |  | 49 | 28 |  | 31 | 0 | 56
|  |  | 10 | 40 | 23 | 26 | 30.5 |  | 33 | 10 |  | 45 | 27.5 |  | 29 | 10 | 53
|  |  | 20 | 36 | 22 | 24 | 28 |  | 25.5 | 20 |  | 41 | 27 |  | 27.5 | 20 | 52
|  |  | 30 | 32 | 21 | 22 | 26 |  | 14 | 30 |  | 38 | 26 |  | 24 | 30 | 50
|  |  | 40 | 28 | 19 | 18 | 25 |  |  | 40 |  | 34 | 24 |  | 22 | 40 | 47
|  |  | 50 | 25 | 16 | 16 | 20 |  |  | 50 |  | 30 | 23 |  | 18 | 50 | 42
|  |  | 60 | 20 | 15 | 13 | 12 |  |  | 60 |  | 27 | 22 |  | 14 | 60 | 38
|  |  | 70 | 15 | 13 | 10 |  |  |  | 70 |  | 24 | 20.5 |  | 10 | 70 | 29
|  |  | 80 | 9 | 10 | 7 |  |  |  | 80 |  | 21 | 18 |  | 5 | 80 | 21
|  |  | 90 |  | 7 | 3.5 |  |  |  | 90 |  | 17 | 17 |  |  | 90 | 9
|  |  | 100 | [6 empty] | 100 |  | 13 | 16